## VMoE (BS 9999)
Stair capacity factors | [8 empty] | Door capacity factors |  |  |  | Notes:
| 1 floor | 2 floors | 3 floors | 4 floors | 5 floors | 6 floors | 7 floors | [5 empty] | Building is sprinkler protected
A1 | 3.9 | 3.4 | 2.95 | 2.45 | 2.15 | 2 | 1.8 |  | A1 | 3.3 |  |  | Building is designed in accordance with BS 9999
A2 | 4.5 | 3.8 | 3.25 | 2.75 | 2.45 | 2.2 | 2 |  | A2 | 3.6 |  |  | Building is provided with fire detection throughout
A3 | 5.4 | 4.6 | 4 | 3.5 | 3.1 | 2.8 | 2.6 |  | A3 | 4.6 |  |  | Building appears to operate a simultaneous evacuation strategy
B1 | 4.2 | 3.6 | 3.1 | 2.6 | 2.3 | 2.1 | 1.9 |  | B1 | 3.6
B2 | 4.8 | 4 | 3.4 | 2.9 | 2.6 | 2.3 | 2.1 |  | B2 | 4.1
B3 | 7 | 6 | 5.3 | 4.6 | 4.2 | 3.7 | 3.4 |  | B3 | 6
Stair capacity factors with enhanced fire protection (15% bonus)
| 1 floor | 2 floors | 3 floors | 4 floors | 5 floors | 6 floors | 7 floors |  | Door capacity factors with enhanced detection (15% bonus)
A1 | 3.315 | 2.89 | 2.5075 | 2.0825 | 1.8275 | 1.7 | 1.53 |  | A1 | 2.805
A2 | 3.825 | 3.23 | 2.7625 | 2.3375 | 2.0825 | 1.87 | 1.7 |  | A2 | 3.06
A3 | 4.59 | 3.91 | 3.4 | 2.975 | 2.635 | 2.38 | 2.21 |  | A3 | 3.91
B1 | 3.57 | 3.06 | 2.635 | 2.21 | 1.955 | 1.785 | 1.615 |  | B1 | 3.06
B2 | 4.08 | 3.4 | 2.89 | 2.465 | 2.21 | 1.955 | 1.785 |  | B2 | 3.485
B3 | 5.95 | 5.1 | 4.505 | 3.91 | 3.57 | 3.145 | 2.89 |  | B3 | 5.1
Building | Stair No. | Clear Width (mm) | Floors served (above ground) | Stair capacity factor | Capacity | Capacity per floor | Lobbied? | Storey exit capacity |  |  | Final Exit | Capacity | Capacity per floor (upper floors) | merging flow capacity | Ground merging flow | Notes
Block 1 | Stair 01 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 62 | 31 | Firefighting shaft
Block 1 | Stair 02 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 240 | 120
Block 1 | Stair 03 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 240 | 120
Block 1 | Stair 04 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 62 | 31 | Firefighting shaft
Block 2 | Stair 05 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 240 | 120
Block 2 | Stair 06 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 240 | 120
Block 2 | Stair 07 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 62 | 31 | Firefighting shaft
Block 2 | Stair 08 | 1100 | 6 | 1.7 | 647.0588 | 107 | Yes | 178 |  |  | 1500 | 647.0588 | 107 | 62 | 31 | Firefighting shaft
Block 3 | Stair 09 | 1100 | 4 | 2.0825 | 528.2113 | 132 | Yes | 178 |  |  | 1500 | 528.2113 | 132 | 240 | 120
Block 3 | Stair 10 | 1100 | 4 | 2.0825 | 528.2113 | 132 | Yes | 178 |  |  | 1500 | 528.2113 | 132 | 62 | 31 | Firefighting shaft
Block 3 | Stair 11 | 1100 | 4 | 2.0825 | 528.2113 | 132 | Yes | 178 |  |  | 1500 | 528.2113 | 132 | 62 | 31 | Firefighting shaft
Block 3 | Stair 12 | 1100 | 4 | 2.0825 | 528.2113 | 132 | Yes | 178 |  |  | 1500 | 528.2113 | 132 | 240 | 120
| Block 1 | Block 2 | Block 3 |  | Notes
Ground + basement | 604 | 604 | 604 |  |  | Based on GF storey exits and merging flows |  |  |  |  | Level | Area (m2) | Population (@ 6m2/person) | Population (@ 10m2/person) | Acutal capacity density
First | 428 | 428 | 528 | [7 empty] | 6 (Blocks A & B only) | 3300 | 550 | 330 | 3.8551
Second | 428 | 428 | 528 | [7 empty] | 5 (Blocks A & B only) | 4680 | 780 | 468 | 5.4673
Third | 428 | 428 | 528 | [7 empty] | 4 | 8060 | 1343.3333 | 806 | 5.8237
Fourth | 428 | 428 | 528 | [7 empty] | 3 | 8060 | 1343.3333 | 806 | 5.8237
Fifth | 428 | 428 | - | [7 empty] | 2 | 8060 | 1343.3333 | 806 | 5.8237
Sixth | 428 | 428 | - | [7 empty] | 1 | 7960 | 1326.6667 | 796 | 5.7514
[11 empty] | G | 7380 | 1230 | 738 | 4.0728
Total | 3172 | 3172 | 2716 | [7 empty] | TOTAL | 47500 | 7916.6667 | 4750 | #DIV/0!
9060

## VMoE (ADB)
|  |  |  | Floors served | Width (mm) | Capacity
Stair capacity equation | P=200W+50(W-0.3)(N-1) |  |  | 10 | 1200 | 645
Stair capacity Table
| Clear width (mm) | [8 empty] | Clear width | Capacity |  |  |  | Notes:
Floors | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600 | 1700 | 1800 | 750 | 60 |  |  |  | Building is sprinkler protected
1 | 150 | 220 | 240 | 260 | 280 | 300 | 320 | 340 | 360 | 850 | 110 |  |  |  | Building is designed in accordance with ADB
2 | 190 | 260 | 285 | 310 | 335 | 360 | 385 | 410 | 435 | 1050 | 220 |  |  |  | Building is provided with fire detection throughout
3 | 230 | 300 | 330 | 360 | 390 | 420 | 450 | 480 | 510 | >1,050 | 1 person / 5mm |  |  |  | Building appears to operate a simultaneous evacuation strategy
4 | 270 | 340 | 375 | 410 | 445 | 480 | 515 | 550 | 585
5 | 310 | 380 | 420 | 460 | 500 | 540 | 580 | 620 | 660
6 | 350 | 420 | 465 | 510 | 555 | 600 | 645 | 690 | 735
7 | 390 | 460 | 510 | 560 | 610 | 660 | 710 | 760 | 810
8 | 430 | 500 | 555 | 610 | 665 | 720 | 775 | 830 | 885
9 | 470 | 540 | 600 | 660 | 720 | 780 | 840 | 900 | 960
10 | 510 | 580 | 645 | 710 | 775 | 840 | 905 | 970 | 1035
Block | Stair No. | Clear Width (mm) | Floors served (above ground) | Capacity | Capacity per floor | Lobbied? | Storey exit width | Storey exit capacity |  | Final Exit | Capacity | Capacity per floor (upper floors) | Merging flow capacity | Ground merging flow | Notes
Block 1 | Stair 01 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 1 | Stair 02 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 1 | Stair 03 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 1 | Stair 04 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 2 | Stair 05 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 2 | Stair 06 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 2 | Stair 07 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 2 | Stair 08 | 1100 | 6 | 420 | 70 | Yes | 850 | 110 |  | 1500 | 310 | 51 | 135 | 67
Block 3 | Stair 09 | 1100 | 4 | 340 | 85 | Yes | 850 | 110 |  | 1500 | 310 | 77 | 135 | 67
Block 3 | Stair 10 | 1100 | 4 | 340 | 85 | Yes | 850 | 110 |  | 1500 | 310 | 77 | 135 | 67
Block 3 | Stair 11 | 1100 | 4 | 340 | 85 | Yes | 850 | 110 |  | 1500 | 310 | 77 | 135 | 67
Block 3 | Stair 12 | 1100 | 4 | 340 | 85 | Yes | 850 | 110 |  | 1500 | 310 | 77 | 135 | 67
| Block 1 | Block 2 | Block 3 |  | Notes
Ground + basement | 540 | 540 | 540 |  |  | Based on GF storey exits and merging flows |  |  |  | Level | Area (m2) | Population (@ 6m2/person) | Population (@ 10m2/person) | Acutal capacity density
First | 280 | 280 | 340 | [6 empty] | 6 (Blocks A & B only) | 3300 | 550 | 330 | 5.8929
Second | 280 | 280 | 340 | [6 empty] | 5 (Blocks A & B only) | 4680 | 780 | 468 | 8.3571
Third | 280 | 280 | 340 | [6 empty] | 4 | 8060 | 1343.3333 | 806 | 8.9556
Fourth | 280 | 280 | 340 | [6 empty] | 3 | 8060 | 1343.3333 | 806 | 8.9556
Fifth | 280 | 280 | - | [6 empty] | 2 | 8060 | 1343.3333 | 806 | 8.9556
Sixth | 280 | 280 | - | [6 empty] | 1 | 7960 | 1326.6667 | 796 | 8.8444
[10 empty] | G | 7380 | 1230 | 738 | 4.5556
Total | 2220 | 2220 | 1900 | [6 empty] | TOTAL | 47500 | 7916.6667 | 4750 | #DIV/0!
6340